STP

Database Design & Alert Reference

# Part 1 — Database Sch

Six purpose-built tables. Each serves a specific role for the dashboard or chatbot. All data originates from the 27 raw PLC columns plus derived columns computed at ingest time

## 1.0  Table Overview

| Table | Role | Granularity | Purpose |
| --- | --- | --- | --- |
| readings_wide | Core | 1 row / minute | Raw PLC columns + all derived columns. Foundation for every other table. |
| pump_sessions | Operational | 1 row / ON cycle | Every continuous run period per pump. Enables runtime and cycling queries. |
| daily_summary | Aggregated | 1 row / day | Pre-computed daily KPIs. Fast dashboard cards and historical trend queries. |
| hourly_profile | Aggregated | 1 row / hour | Hourly averages per day. Powers 24-hour trend charts and peak-hour analysis. |
| alerts_log | Events | 1 row / alert | Every alert event with rule, severity, and resolution status. |
| pump_health | Maintenance | 1 row / pump / day | Daily pump health metrics including efficiency slope. Drives maintenance scheduling. |

## 1.1  Build Order & Dependency Chain

Tables must be built in this exact sequence during each ingest cycle. Each depends on the one before it.

| Step | Table | What to Do | Depends On |
| --- | --- | --- | --- |
| 1 | readings_wide | Load CSV, clean markers (keep B + S), compute all derived columns, save. | Foundation — no dependencies. |
| 2 | pump_sessions | Scan readings_wide ONOFF transitions to build session rows. Close open sessions when ONOFF flips to 0. | Step 1 |
| 3 | alerts_log | Scan readings_wide flag columns. Insert one alert row per flag trigger event. | Step 1 |
| 4 | hourly_profile | GROUP readings_wide BY date, hour. Aggregate per hour. | Step 1 |
| 5 | daily_summary | GROUP readings_wide BY date. Join session counts from pump_sessions. | Steps 1, 2 |
| 6 | pump_health | GROUP pump_sessions BY pump, date. Compute efficiency_slope_7d and health_score. | Steps 2, 5 |

## 1.2  readings_wide

The master table. One row per minute. Contains all raw PLC columns plus every derived column. Every other table is built from this. Keep only Marker = B or S rows. Floor timestamp to the nearest minute at ingest.

| Column | Type | Source | Description |
| --- | --- | --- | --- |
| Raw PLC Columns |  |  |  |
| Timestamp | TEXT | PK | Primary key — YYYY-MM-DD HH:MM:SS |
| Marker | TEXT | Raw | B = Begin row (kept). S = Single (kept). Others discarded at ingest. |
| [PLC]FIT101_HR.DAY_TOTAL | REAL | Raw | Cumulative flow counter for today. Reset at midnight by PLC. |
| [PLC]FIT101_HR.PER_HR | REAL | Raw | Current flow rate — units per hour. |
| [PLC]HLT101.OUTPUT | REAL | Raw | High Level Tank water level in raw units. |
| [PLC]P1.ONOFF … P6.ONOFF | INT | Raw | 1 = ON, 0 = OFF command issued by PLC for each pump. |
| [PLC]P1KWH_HR.PER_HR … P6KWH | REAL | Raw | Energy consumption kWh/hr per pump when running. |
| [PLC]P01A.RHR / RMIN … P01F | REAL | Raw | Runtime hours + minutes per pump. P01A = Pump 1, P01F = Pump 6. |
| date | TEXT | Derived | YYYY-MM-DD extracted from Timestamp. Used for daily joins. |
| Derived — Time |  |  |  |
| hour | INT | Derived | 0–23 extracted from Timestamp. Used for hourly aggregations. |
| day_of_week | INT | Derived | 0 = Sunday … 6 = Saturday. |
| is_weekend | INT | Derived | 1 if Saturday or Sunday, else 0. |
| is_peak_hour | INT | Derived | 1 during peak electricity tariff hours (06–10 and 17–21). |
| pumps_on_count | INT | Derived | Count of pumps with ONOFF = 1 at this minute. |
| Derived — Pump State |  |  |  |
| total_kw | REAL | Derived | Sum of all PxKWH_HR.PER_HR — total station power draw. |
| flow_per_pump | REAL | Derived | FIT101_PER_HR divided by pumps_on_count. NULL if no pumps ON. |
| energy_per_flow | REAL | Derived | total_kw / FIT101_PER_HR — efficiency ratio. Higher = worse. |
| hlt_pct | REAL | Derived | HLT101.OUTPUT as % of historical maximum. Used for threshold alerts. |
| Derived — Tank |  |  |  |
| hlt_diff | REAL | Derived | HLT level change versus previous minute. Positive = filling, negative = draining. |
| flow_diff | REAL | Derived | FIT101_PER_HR change versus previous minute. Detects sudden spikes or crashes. |
| Derived — Flow & Slope |  |  |  |
| flow_z_score | REAL | Derived | Standard deviations from 60-min rolling mean. Computed at ingest; mean not stored. |
| flow_slope_10 | REAL | Derived | Linear regression slope of flow over last 10 minutes (numpy.polyfit). Positive = rising, negative = falling. |
| flag_zero_flow_pump_on | INT | Derived | 1 if any pump ON but FIT101 = 0 for > 2 minutes. Triggers alert B-01 / B-02. |
| Alert Flag Columns |  |  |  |
| flag_flow_anomaly | INT | Derived | 1 if flow_z_score > 3.5 or < -3.5. Triggers C-02 / C-03. |
| flag_hlt_critical_low | INT | Derived | 1 if hlt_pct < 15%. Triggers D-01. |
| flag_hlt_overflow_risk | INT | Derived | 1 if hlt_pct > 90% with pumps ON and hlt_diff > 0. Triggers D-03. |
| flag_short_cycle | INT | Derived | 1 if any pump has > 4 start events in the last 60 minutes. Triggers E-03. |
| flag_pump_overrun | INT | Derived | 1 if any pump session exceeds 20 continuous hours. Triggers E-01. |
| flag_peak_hour_waste | INT | Derived | 1 if is_peak_hour = 1 and hlt_pct > 80% and pumps ON. Triggers G-01. |

## 1.3  pump_sessions

One row per continuous ON period per pump. Built by scanning ONOFF column transitions in readings_wide. Answers chatbot questions about current runtime, longest session, start counts, and per-pump efficiency.

| Column | Type | Source | Description |
| --- | --- | --- | --- |
| id | INT | PK | Auto-increment row ID. |
| pump | TEXT | Derived | Pump identifier: P1, P2, P3, P4, P5, or P6. |
| start_time | TEXT | Derived | Timestamp when pump transitioned from OFF to ON. |
| end_time | TEXT | Derived | Timestamp when pump turned OFF. NULL if still running now. |
| duration_min | INT | Derived | Session length in minutes. Calculated on session close. |
| status | TEXT | Derived | "running" if end_time IS NULL, else "completed". |
| date | TEXT | Derived | Date of session start. Used for daily joins. |
| kwh_consumed | REAL | Derived | Total energy drawn during this session (integrated from PxKWH_HR). |
| flow_during_run | REAL | Derived | Average FIT101_PER_HR while this pump was ON. |
| efficiency | REAL | Derived | flow_during_run / kwh_consumed. Higher = better performing pump. |
| is_short_cycle | INT | Derived | 1 if duration_min < 5. Short cycles risk contactor wear. |

## 1.4  daily_summary

One row per calendar day. Primary key is date (YYYY-MM-DD) — not a timestamp. Pre-computed aggregations so dashboard KPI cards load instantly without scanning readings_wide. Also the source for 7-day and 30-day trend queries.

| Column | Type | Source | Description |
| --- | --- | --- | --- |
| date | TEXT | PK | YYYY-MM-DD — one row per calendar day. Primary key. |
| total_flow | REAL | Derived | MAX([PLC]FIT101_HR.DAY_TOTAL) for that day — total volume pumped. |
| avg_flow_per_hr | REAL | Derived | Average hourly flow rate across the day. |
| peak_flow | REAL | Derived | Maximum flow rate recorded that day. |
| peak_flow_hour | INT | Derived | Hour (0–23) when peak flow occurred. |
| avg_hlt_level | REAL | Derived | Mean tank level across all minutes of the day. |
| min_hlt_level | REAL | Derived | Lowest tank level recorded — demand stress indicator. |
| max_hlt_level | REAL | Derived | Highest tank level recorded. |
| total_kwh | REAL | Derived | Total energy consumed across all pumps for the day. |
| energy_per_m3 | REAL | Derived | total_kwh / total_flow — primary efficiency KPI. Lower = better. |
| P1_hours_on … P6_hours_on | REAL | Derived | Hours each pump ran that day (6 columns). |
| P1_starts … P6_starts | INT | Derived | Number of ON events per pump that day (6 columns). |
| P1_avg_kwh … P6_avg_kwh | REAL | Derived | Average power draw per pump when running (6 columns). |
| total_alerts | INT | Derived | Count of all alerts generated that day. |
| critical_alerts | INT | Derived | Count of CRITICAL severity alerts — key daily health indicator. |
| peak_pumps_on | INT | Derived | Maximum number of pumps running simultaneously that day. |
| avg_pumps_on | REAL | Derived | Average number of pumps running across the day. |
| is_weekend | INT | Derived | 1 if Saturday or Sunday. Useful for demand pattern comparisons. |

## 1.5  hourly_profile

One row per (date, hour) pair — composite primary key. Powers all 24-hour trend charts on the dashboard. Also used for shift-window queries by filtering on the hour column (e.g. hours 6–14 for morning shift). No separate shift_report table needed.

| Column | Type | Source | Description |
| --- | --- | --- | --- |
| date | TEXT | PK | YYYY-MM-DD — composite primary key with hour. |
| hour | INT | PK | 0–23 — composite primary key with date. |
| avg_flow | REAL | Derived | Average FIT101_PER_HR across all minutes in this hour. |
| total_flow | REAL | Derived | Total flow volume within this hour. |
| avg_hlt | REAL | Derived | Average HLT101 level during this hour. |
| avg_pumps_on | REAL | Derived | Average number of pumps running during this hour. |
| total_kwh | REAL | Derived | Total energy consumed by all pumps during this hour. |
| P1_on_minutes … P6_on_minutes | INT | Derived | Minutes each pump was ON during this hour (6 columns). |
| alert_count | INT | Derived | Number of alerts triggered during this hour. |
| is_peak_hour | INT | Derived | 1 if this hour falls in the peak electricity tariff window. |

## 1.6  alerts_log

One row per alert event. Populated automatically from the flag columns in readings_wide. Powers the dashboard Active Alerts panel, the Alerts History page, and all chatbot fault-history queries.

| Column | Type | Source | Description |
| --- | --- | --- | --- |
| id | INT | PK | Auto-increment row ID. |
| timestamp | TEXT | Derived | Exact minute the alert condition was first detected. |
| date | TEXT | Derived | Date portion — for daily alert count queries. |
| hour | INT | Derived | Hour portion — for hourly alert pattern analysis. |
| severity | TEXT | Derived | CRITICAL / HIGH / WARNING / INFO. |
| rule | TEXT | Derived | Alert code that fired (e.g. B-01, D-03). Links to alert reference. |
| pump | TEXT | Derived | Affected pump (P1–P6). NULL for system-level alerts. |
| message | TEXT | Derived | Human-readable description for dashboard display and chatbot answers. |
| value_at_trigger | REAL | Derived | Sensor reading that caused the alert (e.g. flow rate, hlt_pct). |
| resolved | INT | Derived | 0 = open (still active), 1 = resolved (condition cleared). |
| resolved_at | TEXT | Derived | Timestamp when the alert condition cleared. NULL if still open. |
| duration_min | INT | Derived | How many minutes the alert condition lasted before resolving. |

## 1.7  pump_health

One row per pump per day. Built from pump_sessions aggregated by pump and date. efficiency_slope_7d replaces a rolling average — it directly answers "is this pump getting worse?" with a signed slope value. Negative slope = degrading performance.

| Column | Type | Source | Description |
| --- | --- | --- | --- |
| date | TEXT | PK | YYYY-MM-DD — composite PK with pump. |
| pump | TEXT | PK | P1–P6 — composite PK with date. |
| total_runtime_min | INT | Derived | Total ON minutes for this pump on this day. |
| start_count | INT | Derived | Number of ON events (start events) this day. |
| stop_count | INT | Derived | Number of OFF events this day. Should equal start_count ± 1. |
| short_cycle_count | INT | Derived | Sessions under 5 minutes. High count = contactor wear risk. |
| longest_run_min | INT | Derived | Longest single continuous ON session this day. |
| avg_run_min | REAL | Derived | Average session duration in minutes. |
| avg_kwh | REAL | Derived | Average energy draw when running. Baseline for overcurrent detection. |
| avg_flow_per_kwh | REAL | Derived | Flow delivered per kWh consumed. Primary efficiency metric — higher is better. |
| efficiency_slope_7d | REAL | Derived | Linear regression slope of avg_flow_per_kwh over last 7 days. Negative = degrading performance. Replaces rolling average. |
| overrun_flag | INT | Derived | 1 if pump ran > 20 continuous hours. Feeds E-01 alert. |
| health_score | REAL | Derived | Composite score 0–100 combining efficiency slope, short cycles, and overrun. Lower = maintenance needed sooner. |

PUMP STATION MONITORING

Alert Reference

──────────────────────────────────────────────

46 Active Alerts

✅ Part 1 — Active Alerts 46 alerts fully calculable from the current schema and config.py constants. Ready to implement immediately.

## Severity Levels

| Level | Colour | Meaning | Required Response |
| --- | --- | --- | --- |
| CRITICAL | Dark Red | Imminent equipment damage, service disruption, or safety risk | Immediate action within minutes. Phone or SMS operator. |
| HIGH | Red | Serious fault — service at risk if not addressed promptly | Within 30 minutes. Escalate if unresolved. |
| WARNING | Amber | Abnormal condition that may worsen — investigate this shift | Within current shift. Log and monitor. |
| INFO | Blue | Noteworthy — not immediately harmful but worth tracking | Review at end of shift. No immediate action needed. |

## Count by Group

| Group | CRIT | HIGH | WARN | INFO | Active |
| --- | --- | --- | --- | --- | --- |
| A — Power Supply | 2 | — | — | 1 | 5 |
| B — Pump Faults | 3 | 3 | — | — | 7 |
| C — Flow Anomalies | — | 2 | 5 | — | 7 |
| D — HLT Tank | 2 | 4 | 1 | — | 7 |
| E — Runtime & Wear | — | 1 | 2 | 1 | 5 |
| F — Data Quality | — | 2 | 3 | 1 | 6 |
| G — Energy | — | 1 | 1 | 2 | 4 |
| H — Cascade | 3 | 1 | 1 | — | 5 |
| TOTAL | 10 | 14 | 13 | 5 | 46 |

# Part 1 — Active Alerts  (42)

All 46 alerts below are fully calculable from the current schema and config.py constants. No schema changes are needed to implement any of these. Alerts derived from config.py are marked with [config.py: constant_name].

| Code | Alert Name | Severity | Condition — When It Fires |
| --- | --- | --- | --- |
| Group A — Power Supply |  |  |  |
| A-01 | Complete Power Outage | CRITICAL | All Px_ONOFF=0 and all Px_KWH=0 suddenly while HLT is falling |
| A-02 | Partial Power Failure — Circuit Lost | CRITICAL | One Px_ONOFF=1 but Px_KWH=0; other pumps draw normal KWH |
| A-05 | Electricity Present — No Pumps Commanded | INFO | KWH>0 confirmed in history, but all ONOFF=0 for >30 min and HLT<50% |
| A-04 | Power Fluctuation — Unstable Supply | WARNING | Px_KWH varies >30% in consecutive minutes without any ONOFF change |
| A-03 | Power Restored After Outage | INFO | Transition: all KWH=0 (A-01 active) → any KWH>0 within 60 min |
| Group B — Pump Faults |  |  |  |
| B-01 | Pump Tripped — No Power Despite Command | CRITICAL | Px_ONOFF=1 and Px_KWH=0 sustained for >2 min (checked per pump) |
| B-02 | Pump Running — No Flow Output | HIGH | Px_ONOFF=1, Px_KWH>0, FIT101_PER_HR=0 for >5 min |
| B-03 | Multiple Pumps Running — Still No Flow | CRITICAL | ≥2 pumps ON with KWH>0 but FIT101=0 for >3 min |
| B-04 | Pump Overcurrent — Excessive Power Draw | HIGH | Px_KWH > rated_kw × 1.3 for >5 min [config.py: rated_kw] |
| B-05 | Pump Under-Loaded — Abnormally Low Power | WARNING | Px_ONOFF=1, flow>0, Px_KWH < [config.py: rated_kw]× 0.4 for >10 min |
| B-06 | Pump Drawing Power Without Command | HIGH | Px_ONOFF=0 but Px_KWH>0 for >2 min |
| B-07 | All Pumps Simultaneously Tripped | CRITICAL | All Px_ONOFF=1, all Px_KWH=0, pumps_on_count=0 |
| Group C — Flow Anomalies |  |  |  |
| C-01 | Flow Detected — No Pumps Running | HIGH | FIT101_PER_HR>0.1, pumps_on_count=0, all KWH=0 for >3 min |
| C-02 | Flow Spike — Sudden Large Increase | WARNING | flow_z_score > +3.5 AND flow_diff > avg_flow × 0.5 in one minute |
| C-03 | Flow Crash — Sudden Large Decrease | HIGH | flow_z_score < −3.5 while pumps are ON and KWH is normal |
| C-04 | Gradual Flow Decline — Clogging Trend | WARNING | hourly_profile avg_flow down >15% over 48 hrs while total_kwh stable or rising |
| C-05 | Night Flow — No Pumps Commanded | WARNING | hour BETWEEN 22 AND 5, FIT101>0.2, pumps_on_count=0, all KWH=0 |
| C-06 | Flow Sensor Frozen — Stuck Reading | WARNING | FIT101_PER_HR identical for >15 consecutive min while ONOFF states change |
| C-07 | Daily Flow Total Not Advancing | WARNING | FIT101_DAY_TOTAL unchanged for >30 min while FIT101_PER_HR > 0 |
| Group D — HLT Tank |  |  |  |
| D-01 | HLT Critically Low — Emergency | CRITICAL | hlt_pct < 15% AND hlt_diff < 0 for >5 min |
| D-02 | HLT Empty — Service Disruption | CRITICAL | HLT101_OUTPUT < 2% of hlt_physical_max for >2 min [config.py: hlt_physical_max] |
| D-03 | HLT Overflow Risk | HIGH | hlt_pct > 90%, pumps_on_count>0, hlt_diff>0 |
| D-04 | HLT Falling Fast — High Drain Rate | HIGH | hlt_diff < −2 units/min while pumps_on_count=0 |
| D-05 | HLT Not Rising Despite Pumps ON | HIGH | ≥3 pumps ON with KWH>0 but hlt_diff ≤ 0 for >10 min |
| D-06 | HLT Level Sensor Out of Range | HIGH | HLT101_OUTPUT < 0 or > hlt_physical_max × 1.05 [config.py: hlt_physical_max] |
| D-07 | HLT Level Frozen — Sensor Stuck | WARNING | HLT101_OUTPUT identical for >20 consecutive min while pumps change state |
| Group E — Runtime & Wear |  |  |  |
| E-01 | Pump Overrun — Continuous Run Exceeded | WARNING | pump_sessions: single session duration_min > 1200 (20 hours) |
| E-02 | All Pumps ON Simultaneously — Extended | WARNING | pumps_on_count=6 for >120 min AND hlt_diff ≤ 0 (not filling) |
| E-03 | Short Cycling — Single Pump | WARNING | Pump start_count > 4 in 60 min window AND avg session duration < 5 min |
| E-04 | Rapid Short Cycling — Imminent Failure | HIGH | Pump start_count > 10 in 60 min window AND avg session duration < 3 min |
| E-05 | Pump Efficiency Degrading — Maintenance Due | INFO | pump_health: efficiency_slope_7d negative AND avg_flow_per_kwh < 80% of 7-day baseline |
| Group F — Data Quality |  |  |  |
| F-01 | Data Gap — Short Comms Dropout | INFO | Time since last valid reading row: >5 min and ≤30 min |
| F-02 | Data Gap — Extended Outage | HIGH | Time since last valid reading row: >30 min |
| F-03 | Flow Sensor Stuck — Frozen Reading | WARNING | FIT101_PER_HR unchanged for >15 min while ONOFF states change |
| F-04 | HLT Sensor Stuck — Frozen Reading | WARNING | HLT101_OUTPUT unchanged for >20 min while pumps change state |
| F-05 | Impossible Sensor Value | HIGH | FIT101<0 or >fit_max; HLT101<0 or >hlt_max×1.05 [config.py: fit_max, hlt_max] |
| F-06 | KWH Reading Anomaly | WARNING | Px_KWH > rated_kw × 2.0 or Px_KWH negative while Px_ONOFF=1 [config.py: rated_kw] |
| F-07 | Duplicate Timestamp Detected | INFO | Two rows in readings_wide share the same Timestamp value |
| Group G — Energy |  |  |  |
| G-01 | Pumping During Peak Tariff — Tank Full | WARNING | is_peak_hour=1, hlt_pct>80%, pumps_on_count>0, hlt_diff>0 |
| G-02 | Energy Consumed With Zero Flow | HIGH | total_kw>0 but FIT101_PER_HR=0 for >5 min |
| G-03 | Pump Efficiency Drop — Below Slope Baseline | INFO | pump_health: efficiency_slope_7d negative trend AND avg_flow_per_kwh < 80% of rolling avg |
| G-04 | Daily Energy Budget Exceeded | INFO | Cumulative daily total_kwh > configured_daily_budget_kwh [config.py: daily_budget] |
| Group H — Cascade |  |  |  |
| H-01 | Power Outage AND Tank Draining Fast | CRITICAL | A-01 active AND hlt_diff < −1.5 units/min AND hlt_pct < 50% |
| H-02 | Multiple Pumps Tripped — HLT Low | CRITICAL | ≥3 pumps ONOFF=1 with KWH=0 (B-01) AND hlt_pct < 40% |
| H-03 | All Pumps Faulted — Tank Critical | CRITICAL | pumps_on_count=0, all KWH=0, all tripped or off, hlt_pct < 25% |
| H-04 | Night Flow — No Pumps — Sustained | HIGH | hour BETWEEN 22–5, FIT101>0.3, pumps_on_count=0 for >15 min |
| H-05 | Pump Overrun AND Efficiency Dropping | WARNING | E-01 active (session>20 hrs) AND pump_health efficiency_slope_7d is declining |

Config.py needs

rated_kw : rated power of each pump motor

hlt_physical_max: actual physical capacity of the HLT101 tank

fit101_physical_max: maximum measurable flow rate of the FIT101 flow meter

daily_energy_budget_kwh: maximum acceptable electricity consumption per day in kWh